## Slide 1: Multi Housing Radon Dilution Retrofit
a Fresh Air Dilution solution
2019 International Radon Symposium Denver, Colorado

## Slide 2: FACT: Multi-Family Structures are constructed tight with low air exchange rates. RESULT: Radon from building materials accumulates to unacceptable health risk levels in breathing zones.
2019 International Radon Symposium Denver, Colorado

## Slide 3: In Multi-Family Housing Fresh Air / Ventilation has generally been sought by introducing conditioned air into Corridors (serving as fresh air ducts) with the expectation that pressurization would force corridor fresh air to trickle under the doors to provide occupants with sufficient fresh air. Imagine the effect of a fire in the corridor NOT SO GOOD IN PRACTICE . . . But they are still doing it! There is a remarkable continuing opportunity for Radon Mitigators here
2019 International Radon Symposium Denver, Colorado

## Slide 4: The Common, Traditional Multi-Housing Fresh Air Solution?
Pressurize the corridor “duct” with conditioned air to trickle “fresh” corridor air into each unit under the doors
Corridor
Pressurized
with rarely filtered
rooftop air
Bird Congregations, Nests, feather collections and bird Graveyards
Dwelling
Dwelling
2019 International Radon Symposium Denver, Colorado

## Slide 5
2019 International Radon Symposium Denver, Colorado
The corridors’ “fresh” air trickling under the suite doors will satisfy occupants’ needs for fresh air and for radon reduction?
Really?
What are the FACTS?

## Slide 6
2019 International Radon Symposium Denver, Colorado
Ventilation in Multi-Family Buildings 19th Annual Westford Symposium on Building Science
The FACTS:

## Slide 7: What does Lorne Ricketts MASC say the evidence means?
Most Apartments / condos (multifamily buildings) are ventilated using pressurized corridor systems
Decades of anecdotal evidence indicates that this system likely does not work very well Still most common system
Particularly relevant now, as newer more airtight buildings have less tolerance for poorly performing ventilation systems Less infiltration and exfiltration to supplement ventilation
QUOTE:
2019 International Radon Symposium Denver, Colorado
https://buildingscience.com/sites/default/files/01.03_2015-08

## Slide 8: Lorne (the scientist) then concludes that research findings support the anecdotes
Corridor pressurization does not provide intended ventilation rates to a large number of suites Some significantly over ventilated while others significantly under ventilated
Significant leakage along the ventilation air flow path from the duct and the corridor (wasted ventilation) Uncontrolled airflow wastes energy and provides poor ventilation
Stack effect and wind pressures are often similar or greater than mechanically-induced pressures Ventilation system can not practically overwhelm nature
QUOTE:
2019 International Radon Symposium Denver, Colorado

## Slide 9: What Lorne Says it Means:
Ventilation air should be directly supplied to suites to limit the potential of loss along the flow path and of the system being overwhelmed by stack effect and wind
The exterior enclosure should be airtight, and suites and verticalized shafts should be compartmentalized (airtight) to limit the impact of wind and stack effect on ventilation
2019 International Radon Symposium Denver, Colorado
QUOTE:

## Slide 10: CONTEXT
International Mechanical Code 2012
  601.2 Air movement in egress corridors shall not serve as supply, return, exhaust, relief or ventilation air ducts.
  Something similar in code since at least 1996
2019 International Radon Symposium Denver, Colorado

## Slide 11: CONTEXT
CaGBC LEED Credit EQ11 Interpretation (#1126)
Supply of ventilation air from corridor is unlikely to meet the referenced ASHRAE 62.1 requirements for distribution
Likely to conflict with ETS and fire separation
Canada Green Building Council
2019 International Radon Symposium Denver, Colorado

## Slide 12
As presented by Lorne Ricketts
2019 International Radon Symposium Denver, Colorado

## Slide 13
As presented by Lorne Ricketts MASC
2019 International Radon Symposium Denver, Colorado

## Slide 14: My Conclusions?
Corridor Pressurization / Ventilation will successfully dilute radon in some of the units some of the time. Not Acceptable
Correct amounts of fresh air injected directly into a compartmentalized unit will always dilute radon in that unit

## Slide 15: My Full Disclosure to Everyone No Secrets, No Patents
Feel free to use any of this information in your own business and to develop your own products and systems
And to expand your business to add fresh air to SSD systems (a very good idea for improved IAQ and customer health, cognitive function and sleep)
Use it to operate your own mechanical ventilation retrofit business expansion to help anyone to meet ASHRAE 62.2-2016-7, IBC and IEC

## Slide 16
2019 International Radon Symposium Denver, Colorado
Make it simple: Plug ‘n Play simplicity
Special (no restoration) port boring rig with effective dust/slurry capture system
No Permits, no electrician, no HVAC or plumbing contractors
Long life, high MERV filter, serviceable from indoors
Adjustable radon level, automatic temperature humidity limiting
Quieter than an HVAC system
Completed from indoors, through masonry blocks, any weather, any floor. Outdoor access NOT needed
No cleanup, restoration of drywall, wall covering, crown moldings, new soffits or new 120 VAC wiring
In and out the door in 1.5 to 2.5 hours (experienced team)
CO2 control-ready
2019 International Radon Symposium Denver, Colorado
This is What I Have Accomplished:

## Slide 17: Radon Reduction Result
Radon levels were reduced from 4.4-18 pCi/l to acceptable levels in every case without over-ventilation
Outdoor Fresh Air Flows / Radon Levels were precisely adjustable from 5-70 CFM with a jeweler’s screwdriver
In most cases, 14-30 cfm constant pressurization / ventilation was all that was required. Usually, reductions in airflow were made following clearance testing
The pushbutton-adjustable temperature/humidity controller operated ventilation to maintain 76-78 degrees, < 60% RH without ever overpowering the HVAC system. It Worked

## Slide 18: Wayne Dean’s Ideas #1-11 :
Idea #1 A system to provide each dwelling unit with filtered fresh air, delivered directly through a port in that unit’s exterior wall Unconditioned but Filtered Air delivered directly into the largest room

## Slide 19: Idea #2 Fresh Air Intake Filter
Provide each unit with a long life, high MERV (14-25) air intake filter serviceable from indoors ASHRAE 62.2-2017

## Slide 20: Idea #3 Low Voltage, Variable Speed, ECM Motorized Impeller

## Slide 21: Idea #4 Manual Radon Level / Speed Adjustable by Jeweler’s Screwdriver

## Slide 22: Idea #5 Deliver Fresh Air in a narrow beam, high in the room, to mix and temper with Indoor air, by way of 0.125” Honeycomb Laminar Air Flow Generator

## Slide 23: Idea #6 Control Temperature and Relative Humidity Automatically

## Slide 24
Idea #7 120 vac Wiring Unnecessary
Power system with 12vdc plug-in power pack
No electrician, permit application, cost, delays, inspections

## Slide 25: Idea #8 Built a Special Port-Boring Rig
Develop a diamond core rig that would bore a precision port through exterior walls
Fully captures all dust and slurry
Does not require any new construction, cleanup or restoration

## Slide 26: Idea #9 Finished Air Intake Port Unmarked, Undamaged Wall No Restoration Necessary Just wipe off a little dust

## Slide 27: Idea #10 Cyclonic Dry Particle Separator Keep Vac Filter from clogging for weeks, not hours Requires High Air Velocity

## Slide 28: Idea #11 Control Ventilation by Electronic IAQ Controllers
Manual electronic adjustable ventilation rate
Adjustable by occupant
Automatically adjustable by Temperature / Humidity controller
Automatically adjustable by CO2 and/or IAQ controller to maintain ideal* 600 ppm CO2
* Harvard School of Public Health Lawrence Berkeley National Laboratory

## Slide 29
2019 International Radon Symposium Denver, Colorado